**19” 24 port module carrier 1 HU, grey**

Module carrier made of metal for 19” rack mount, with integrated cable management for a minimum of 24 cables;

pre-installed bonding wire;

panel accepts a minimum of 24 RJ45 modules;

ports labeled 1 to 24 on panel;

latch of plug pointing upwards for easy unplugging of patch cords;

comes with 24 RJ45 modules Cat.6A which meet or exceed the specifications of IEC 60603-7-51, evidence by certificate;

UL listed, evidence by certificate;

for applications according to ISO/IEC 11801-1, Annex E (10 Gbit/s, PoE Type 2);

optimized contact design to avoid sparcs in the area of data transmission;

metallic latch made of spring steel

IDC contacts eligible for solid and stranded wires;

no need for module-specific tools to terminate wires;

module housing has a flat-pin contact for individual bonding;

detenting clamp for cable strain relief;

separate shield contacts;

arrangement of wires without crossing the pairs possible;

foil of pair shield has to be maintained up to the wire holder in the wire manager.

Optional plug-in dust-shutters in 5 different colours available to denote individual applications.

The permanent link consisting of this module and the horizontal cable as specified elsewhere in this tender has to meet or exceed the specifications of ISO/IEC 11801-1 permanent link class EA; this has to be proven by a link certificate!

**Features:**

RJ45 module

Depth: ≤ 32.0 mm

Width: ≤ 14.8 mm

Performance: IEC 60603-7-51 Cat.6A

Plug compatibility: RJ45, RJ12 and RJ11 plugs,

protection against over-

bending the contacts

Mating cycles: ≥ 750

Cable diameter: ≤ 9 mm

Contacts: 8

Contact design: Optimized design, evidence

provided by data sheet

Wire connection: IDC

Wire diameter: 0.9 – 1.6 mm

Conductor dimensions: solid: AWG26/1–22/1

stranded: AWG27/7–22/7

Pin/pair assignment: T568B

Bonding connection: 2.8 mm DIN 46342-1

Colours for optional dust shutters: black, orange,

green, blue, yellow

Module carrier:

Depth: ≤ 115 mm

Material: sheet steel, powder coated

Color: light grey like RAL 7035

Number of ports: ≥ 24

Number of cable ties: ≥ 24

Manufacturer: Telegärtner

Type: 19“ module carrier 1U

Part No.: 100007013